Interpretations of Standard ANSI/RESNET/ICC 380-2022 apply to the RESNET® HERS®

Interpretation:	Measuring Mechanical Fresh Air

Designation		No: 380-2022-03

Approved:		March 3, 2026 by RESNET® SDC 300

Effective Date:	April 2, 2026

| Request from: |  | Name: |  | Russell Ray |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Affiliation: |  | Houk Air Conditioning |  |  |  |  |  |  |
|  |  | Address: |  | 833 111th Street |  |  |  |  |  |  |
|  |  | City: | Alington |  |  | State: | Texas |  | Zip: | 76011 |
|  |  | Telephone: |  | 817-265-1191 Ext 2150 |  |  |  |  |  |  |
|  |  | E-mail: |  | russellr@houkac.com |  |  |  |  |  |  |
| Reference: |  | This request for interpretation refers to the requirements presented in Standard: |  |  |  |  |  |  |  |  |
|  |  | ANSI/RESNET/ICC 380-2022 |  |  |  |  |  |  |  |  |
|  |  | Page Number(s): |  |  |  |  |  |  |  |  |
|  |  | Section(s): |  |  | Chapter 6 |  |  |  |  |  |
|  |  | Table(s): |  |  |  |  |  |  |  |  |
|  |  | Relating to: |  |  | Measuring Fresh Air |  |  |  |  |  |
| Background: |  |  |  |  |  |  |  |  |  |  |
| Interpretation: |  | Proposed by the petitioner. The tolerance when measuring fresh air for a single-family dwelling is Plus or Minus 15 CFM. |  |  |  |  |  |  |  |  |
| Question: | Is this interpretation correct? |  |  |  |  |  |  |  |  |  |
| SDC Answer: |  | No |  |  |  |  |  |  |  |  |
| SDC Comments: |  | This Standard is focused on how to perform the measurement and how to obtain an accurate measurement, not whether the result is acceptable to the code or program the measurement is being taken for. Maximum errors cited within Chapter 6 are for the purposes of equipment calibration and are not to be extended to on-site measurements. Where fresh air measurements are required by a code or program, the authority requiring the measurements shall specify their accepted tolerances. |  |  |  |  |  |  |  |  |