**Draft PDS-01 MINHERS Addendum 71,**

**SEER2 and HSPF2 Conversions**

***Modify MINHERS Chapter 3 section 303.1 as follows:***

*Add the following Exception:*

**Exception 7:** RESNET Home Energy Ratings shall be calculated using the modifications of Standard ANSI/RESNET/ICC 301-2019 as follows:

***Add the following definitions to standard ANSI/RESNET/ICC 301-2019:***

***Heating Seasonal Performance Factor 2 (HSPF2)*** – A standardized measure of Heat Pump efficiency, based on the total heating output of a Heat Pump in Btu and divided by the total electric energy input in watt-hours and under test conditions specified by the Air Conditioning and Refrigeration Institute Standard 210/240 2023.

***Seasonal Energy Efficiency Ratio 2 (SEER2)*** – A standardized measure of Air Conditioner efficiency based on the total cooling output of an Air Conditioner in Btu/h, divided by the total electric energy input, in Watt-hours, under test conditions specified by the Air Conditioning and Refrigeration Institute Standard 210/240 2023.

1.

*Modify standard ANSI/RESNET/ICC 201-2019 section 4.4.4 as follows:*

* + 1. Air Source Heat Pumps and Air Conditioners.
			1. For Heat Pumps and Air Conditioners where a detailed, hourly HVAC simulation is used to separately model the compressor and evaporator energy (including part-load performance), the back-up heating energy, the distribution fan or blower energy and crank case heating energy, the Manufacturer’s Equipment Performance Rating (HSPF and SEER[[1]](#footnote-1)) shall be modified to represent the performance of the compressor and evaporator components alone.[[2]](#footnote-2) The energy uses of all components, including compressor and distribution fan/blower and crank case heater, shall then be added together to obtain the total energy uses for heating and cooling.

For Heat Pumps and Air Conditioners with the more recent Manufacturer’s Equipment Performance Ratings (HSPF2 and SEER2), these ratings shall be converted to HSPF and SEER values by dividing by the conversion factors in Table 4.4.4.1(1). If the type of equipment is not determined, the conversion shall default to the “Split System” factors. All calculations, including Equation 4.1-1a, shall use values converted to SEER and HSPF.

**Table 4.4.4.1(1) SEER2/HSPF2 Conversion Factors[[3]](#footnote-3)**

| **Equipment Type** | **SEER2/SEER** | **HSPF2/HSPF** |
| --- | --- | --- |
| Split System | 0.95 | 0.85 |
| Single Package | 0.96 | 0.84 |
| Small Duct High Velocity | 1.00 | 0.85 |
| Space Constrained | 0.99 | 0.85 |

1. (Normative Note) For Commercial Variable Refrigerant Flow (VRF) Multi-Split Air Conditioning and Heat Pump Equipment, use IEER in place of SEER. [↑](#footnote-ref-1)
2. (Informative Note) Such approaches are described in Cutler et al. 2011 and Fairey et al. 2004. [↑](#footnote-ref-2)
3. (Informative Note) Conversion factors developed by AHRI, and adopted by RESNET. [↑](#footnote-ref-3)