Comment/Explanation*: 
Include your justification for your proposed change to the draft standard below.
_________________________________________________________________________________________

A manufacturer’s installation or owner’s manual should list the minimum Conditioned Space Volume requirements for the heat pump water heater.  A quick survey of manufacturers installation instructions states minimum Conditioned Space Volumes from 450ft3 – 1,000ft3.  An iHPWH which is installed in the minimum (or greater) conditioned Space Volume as noted in the manufacturer’s installation instructions should receive the maximum allowable effective COP.  If a heat pump water heater requires 750 ft3 per the manufacturer, that heat pump water heater would than be required to use the COPeff equation.

Calculation where ‘6 ac. Where an iHPWH is installed, the rated UEF shall be used to determine the heat pump COP if one of the following conditions is met for each water heater.  In this case a heat pump water heater installed in 750 ft3 per manufacturer’s installation instructions would now be required to utilize ‘For all other iHPWH installations, the maximum allowable effective COP (COPeff) shall be determined by the equation below…’   It appears a HPWH installed per manufacturer’s installation instructions in a space < 1,000 ft3 would be derated.  If this is the case, we strongly recommend language which does not derate the COP of the HPWH if the installation follows the manufacturer's instructions which requires < 1,000 ft3, and have suggested such language in our proposed change to the draft Standard.

Where the minimum Conditioned Space Volume is not specified by the manufacturer, suggest adding ‘the Conditioned Space Volume shall have a volume equal to or greater than 1,000 ft3’.

Proposed Change to the Draft Standard*
Use “strikethrough” and “underline” formatting to indicate all proposed changes. Changes must be shown with “hard-formatting” strikethrough and underline, not “track changes”.

Use a color other than red to indicate proposed changes to the draft.
____________________________________________________________________________________________

- A ducted intake and ducted exhaust are both is installed directly connecting the iHPWH to a space within the Conditioned Space Volume of the Dwelling Unit according to the manufacturer’s installation instructions.  Where the minimum Conditioned Space Volume is not specified by the manufacturer, the Conditioned Space Volume shall haveing a volume equal to or greater than 1,000 ft3. and tThe incoming air is drawn from the same space as the space to which the exhaust is discharged and this space is different than the space containing the iHPWH.