Comment/Explanation*: 
Include your justification for your proposed change to the draft standard below.
_________________________________________________________________________________________

Split system heat pump water heaters can be installed indoors, and would be subject to the same containment volume (ft3) and the net free opening area (in2) and ducting requirements as iHPWHs.  If installed outdoors, the heat pump compressor shall have sufficient ventilation and the storage tank shall be located as close as practible to the heat pump compressor.  In the split system heat pump water heater’s installation manuals the manufacturers note if the unit is not able to operate with adequate airflow due to obstacles and reduced clearances, then heating input will be reduced by approximately 10% and power consumption increased by approximately 10%.

Proposed Change to the Draft Standard*
Use “strikethrough” and “underline” formatting to indicate all proposed changes. Changes must be shown with “hard-formatting” strikethrough and underline, not “track changes”.

Use a color other than red to indicate proposed changes to the draft.
____________________________________________________________________________________________

Integrated Heat Pump Water Heater – For Integrated Heat Pump Water Heaters, record whether the system has a ducted intake and exhaust and record the spaces to and from which the air is ducted. If not ducted, for the space that contains the iHPWH, measure dimensions of the room to calculate its volume (ft3) and record the total net free opening area (in2) of any grilles/louvers/door undercuts. Where the net free area of a grille or louvered opening is not specified by the manufacturer, the net free area shall be calculated as 35% of the area of the grille or louvered opening.

Split System Heat Pump Water Heater – For Split System Heat Pump Water Heaters, record the location of both the heat pump and the storage tank. If the heat pump is located indoors, record whether the system has a ducted intake and exhaust and record the spaces to and from which the air is ducted.  If not ducted, for the space that contains the heat pump, measure dimensions of the room to calculate its volume (ft3) and record the total net free opening area (in2) of any grilles/louvers/door undercuts. Where the net free area of a grille or louvered opening is not specified by the manufacturer, the net free area shall be calculated as 35% of the area of the grille or louvered opening.