Comment/Explanation*: 
Include your justification for your proposed change to the draft standard below.
_________________________________________________________________________________________

Split system heat pump water heaters can be installed indoors, and would be subject to the same containment volume (ft3) and the net free opening area (in2) and ducting requirements as iHPWHs.  If installed outdoors, the heat pump compressor shall have sufficient ventilation and the storage tank shall be located as close as practible to the heat pump compressor.  In the split system heat pump water heater’s installation manuals the manufacturers note if the unit is not able to operate with adequate airflow due to obstacles and reduced clearances, then heating input will be reduced by approximately 10% and power consumption increased by approximately 10%.

Proposed Change to the Draft Standard*
Use “strikethrough” and “underline” formatting to indicate all proposed changes. Changes must be shown with “hard-formatting” strikethrough and underline, not “track changes”.

Use a color other than red to indicate proposed changes to the draft.
____________________________________________________________________________________________

For Integrated Heat Pump Water Heaters – containment volume (ft3) and the net free opening area (in2) of the space containing the water heater. If ducted, the space to which the exhaust air is discharged and the space from which the intake air is supplied.

For Split System Heat Pump Water Heaters - the location of both the heat pump and the storage tank. If the heat pump compressor is installed outdoors, the heat pump compressor shall be installed in an area which allows sufficient ventilation according to the manufacturer’s installation instructions.  The heat pump compressor must be located as close as practible to the storage tank unit but no further than the manufacturer’s installation instructions.  If the split system heat pump water heater is installed indoors, containment volume (ft3) and the net free opening area (in2) of the space containing the water heater. If ducted, the space to which the exhaust air is discharged and the space from which the intake air is supplied.