Comment/Explanation*: 
Include your justification for your proposed change to the draft standard below.
_________________________________________________________________________________________

Draft PDS-03 RESNET® HERS Addendum 77, Integrated Heat Pump Water Heater (iHPWH)

Additional inputs for air source heat pump domestic water heaters need to be based upon readily available information so as not to overburden Raters with researching values that may not be available. Such is the case with the proposing an input for Water Heater capacity in BTU/hr or kBTU/hr. This information is not readily available on most of the fiamilair document resources such as AHRI certifictes, Energy Star data or MFR”s Specificaiton data. The input should be based on upon Input power in Kw which is readily available.

Proposed Change to the Draft Standard*
Use “strikethrough” and “underline” formatting to indicate all proposed changes. Changes must be shown with “hard-formatting” strikethrough and underline, not “track changes”.

Use a color other than red to indicate proposed changes to the draft.
____________________________________________________________________________________________

- The enclosed space containing the water heater is verified to have a total net free opening area to an adjacent heated or conditioned space that is no less than the sum of 125 in2 plus 25 in2 per KW of Water Heater Input Power of no less than 75 in2 per 100 watts of compressor power, using any combination of grilles, louvers, door undercuts, or a louvered door. Where the compressor capacity power is not specified by the manufacturer, the total net free opening area shall be no less than 560 in2. The sum of the enclosed space and adjacent connected space shall have a combined space volume equal to or greater than 1,000 ft3.